l---+--LT1----+-T--2----T----3--T-+----4T---+---T5----+-T--6----T----7--R-+----r

|

|

|

|

|

|

|

|

|

|       LOADCALC

|

|       Copyright 1991-93, by Robert J. La Capra

|       All Rights Reserved

|

|       Shareware Version 1.1

|

|

|

|

|

|

|

|

|

|

|

|

|

|

|

|

|

|

|       Robert J. La Capra

|       50 Hillside Terrace

|       Andover, NJ 07821

|

|

|

|

|

|

|

|

|

|

|

|

|

-- Table Of Contents --

Shareware ................................................ I

Disclaimer .............................................. II

Included Files .......................................... II

Introduction ............................................. 1

MENUS - Main And Function ................................ 2

DATA INPUT ............................................... 2

CONTEXT SENSITIVE HELP ................................... 3

ERROR MESSAGES ........................................... 3

SERVICE/FEEDER CALCULATIONS .............................. 3

REFERENCE TABLES

Grounding Electrode Conductors ...................... 7

Service/Feeder Conductors ........................... 7

SETUP

Color Defaults ...................................... 7

Registration Information ................................. 8

Registration form ....................................... 10

Other Electrical Software Available ..................... 11

=  Shareware  =

Shareware is a term used to describe a software distribution or

marketing method. Under the shareware concept, software may be

freely copied and passed along to others, or distributed through

bulletin board systems, shareware distributors, etc...

As a recipient of a shareware program, you may use the software

for a short trial period to determine if it meets your needs. If

it does, you must pay the registration fee to the author of the

program. By paying the fee, you are granted the right to retain

the software for your own use. If the software is not suitable,

then you are not obligated to pay the fee, but you must not

continue to use the program.

The shareware system provides substantial benefits to you:

1. You get to try out the software before you buy it.

2. Shareware is much less expensive than comparable commercial

packages. You don't pay for marketing and packaging.

3. Many programs have been developed by expert programmers who

would never consider marketing their products commercially.

All they ask in return is a small fee to compensate them for

the considerable time and effort they have invested in the

development, testing and support of their products.

4. Shareware authors are much more responsive to the users'

requests for bug fixes, added features, special modifications,

etc...

The system is based entirely on the honor system, and usually

works well. Most people are honest and wouldn't violate the trust

placed in them by the author of the software.

Shareware is not free software. The author counts on your

integrity. If you intend to continue to use the program, please

register using the form at the end of this manual, or the form

included in the file "LOADCALC.REG". Registration entitles you to

an expanded, 'Registered-User' version of this program. See the

end of this manual for details.

I

*  DISCLAIMER OF WARRANTY  *

|

| THIS SOFTWARE AND DOCUMENT ARE OFFERED "AS IS" AND WITHOUT

| WARRANTIES AS TO PERFORMANCE OF MERCHANTABILITY OR ANY OTHER

| WARRANTIES WHETHER EXPRESSED OR IMPLIED. BECAUSE OF THE VARIOUS

| HARDWARE AND SOFTWARE ENVIRONMENTS INTO WHICH THIS PROGRAM MAY

| BE PUT, NO WARRANTY OF FITNESS FOR A PARTICULAR PURPOSE IS

| OFFERED.

|

| GOOD DATA PROCESSING PROCEDURE DICTATES THAT ANY PROGRAM BE

| THOROUGHLY TESTED BEFORE RELYING ON IT. THE USER MUST ASSUME

| THE ENTIRE RISK OF USING THIS PROGRAM. THE AUTHOR OF THIS

| PROGRAM ASSUMES NO LIABILITY.

|

| DUE TO THE NATURE OF THIS PROGRAM, THE USER MUST BE FAMILIAR

| WITH THE SAFETY CONSIDERATIONS OF DESIGNING AND SAFELY

| INSTALLING ELECTRICAL WIRING SYSTEMS, IN ACCORDANCE WITH THE

| NATIONAL ELECTRICAL CODE. THIS PROGRAM IS NOT INTENDED TO

| REPLACE THE NEED FOR A QUALIFIED PERSON WHO IS EXPERIENCED IN

| THE ELECTRICAL DESIGN, CONSTRUCTION AND MAINTENANCE OF SAID

| ELECTRICAL SYSTEMS IN THEIR ENTIRETY.

|

|

|

|

|

|

| FILES INCLUDED ON LOADCALC SHAREWARE DISK :

| -------------------------------------------------------

| LOADCALC.DOC          This documentation file

| LOADCALC.EXE          LOADCALC program

| LOADCALC.REG          Registration form

| READ.ME               License agreement

|

|

|

| The importance of making a working copy of this or any other

| program disk cannot be too strongly stressed ! Please STOP NOW

| and copy all files included on the original LOADCALC disk to a

| blank formatted disk, and place the original in a secure place.

II

Introduction:

-------------

LOADCALC is designed to perform service/feeder load calculations

for single dwelling units in accordance with the 1993 National

Electrical Code requirements.

Functions supported in this shareware version:

* Optional method of single dwelling units as per NEC 220-30

* Allowance of all standard loads, as well as:

Input of 2 additional user-defined appliance loads (motor or

nonmotor, fixed or portable), and,

Input of 1 additional user-defined lighting load (continuous or

noncontinuous)

* Context sensitive help at any data input field, describing the

expected input, any special definitions or requirements relating

to that data, and the NEC Article/Section if applicable.

* Quick reference tables for:

Grounding Electrode Conductor Sizes

Service/Feeder Conductor Sizes

* LOADCALC operates with 'what-if' capability. You can quickly

and easily change only the data you wish to, without having to

start a new calculation and re-enter all the required data.

Results are calculated and displayed as you make each change.

* Screen report showing all loads selected, their va values, all

applicable demand factors, the total net computed load in va and

amperes, and the minimum allowable service\feeder size.

** All functions conform to the 1993 National Electrical Code. **

The National Electrical Code is a copyrighted document of the

National Fire Protection Association, Batterymarch Park, Quincy,

MA. 02269.

Page 1

MAIN MENU:

----------

To run LOADCALC, type LOADCALC then press ENTER or RETURN.

In this shareware version, upon startup of the program, you will

see an opening screen showing copyright information and a message

about this software. Towards the bottom of the screen there will

be a number printed with an input area below it. Enter the number

at the input area exactly as it appears. LOADCALC will then run.

The main menu is a pull down type, structured as a horizontal bar

at the top of the screen with main titles displayed. Each of these

main titles represents a sub menu with one or more related program

functions.

To select specific program functions :

1. Press the hilighted letter of the menu item (main or sub).

OR,

2. Press the DOWN ARROW key to open the first sub menu, then use

LEFT or RIGHT ARROW keys to move between sub menus.

OR,

3. Position the hilighted block over a menu selection (main or

sub), then press ENTER.

DATA INPUT:

-----------

LOADCALC has 'What-If' data entry routines. This method of data

input and calculation allows you to instantly see the results of

changing one data item at a time. You will not need to restart the

function from the beginning and re-enter all data just to see the

effect of changing one parameter.

Use the UP and DOWN ARROW, TAB & SHIFT+TAB keys, or ENTER, to move

between input fields, entering data as you go. Some fields limit

your input to certain values, and if you input data that is

unacceptable, you will hear a beep and will not be able to move

from that field until the correct data has been entered (or you

leave the field empty).

Some routines require that you select one data item from a list of

choices. Use the UP or DOWN ARROW keys to position the hilighted

bar over your choice and press ENTER.

After you have entered all required data, the calculation will be

performed and displayed. You can then change individual data items

and instantly see the results.

CAUTION:

When entering the last data item, or changing one data item which

was previously entered:

Be sure to record that change by moving from that field to another

field, or by pressing ENTER while still on that field.

Page 2

CONTEXT SENSITIVE HELP:

-----------------------

Help is available at any input field and at any routine which

requires selecting one item from a list of choices, by pressing

the F1 function key. A window will open with help instructions

pertaining to that field.

If applicable, a NEC Article/Section number will also print as the

last line in the help window, referring you to the appropriate

section of the 1993 NEC.

To remove the help window, press ENTER. You will be returned to

the data input area.

ERROR MESSAGES:

---------------

If certain restrictions apply to a particular data item that you

have entered, and the restrictions have not been met, a window

will open with an error message pertaining to the data entered

into that field.

If applicable, a NEC Article/Section number will also print as the

last line in the error message window, referring you to the

appropriate section of the 1999 NEC.

To remove the error message window, press ENTER. You will be

returned to the data input area.

SERVICE/FEEDER CALCULATIONS:

----------------------------

Optional Method:

----------------

LOADCALC will compute the net computed load and the minimum

service entrance or feeder size for single dwelling units. This

shareware version supports the optional calculation method as per

the National Electric Code, NEC 220-30. The registered-user

version also supports the standard method.

NEC 220-30 allows the use of the optional method for single

dwelling units with the total connected load served by a single 3-

wire, 120/240 volt or 208Y/120 volt set of service-entrance or

feeder conductors with an ampacity of 100 or greater. This version

of LOADCALC supports 120/240 volt.

Page 3

The optional method is applied as follows:

The sum of the va ratings of the following loads is computed:

1  1500 va for each 20 ampere small appliance branch circuit

serving the kitchen, dining room, etc.

2  1500 va for each 20 ampere laundry branch circuit serving

the laundry area.

3  3 va per square foot for general lighting and general use

receptacles.

4  The nameplate ratings of all fastened-in-place appliances,

ranges, wall mounted ovens, counter mounted cooking units,

dryers, and water heaters.

5  The nameplate va ratings of all motors and any additional

lighting loads not included in the general lighting load.

This total is referred to as the 'other' load.

If the sum of the 'other' load exceeds 10000 va, then the first

10000 va of the 'other' load is taken at 100% and added to 40% of

the remainder of the 'other' load that is above 10000 va. This new

value is the 'other demand' load.

If the sum of the 'other' load is less than or equal to 10000 va,

then the sum of the 'other' load is taken at 100%. This value is

the 'other demand' load.

This computed va value for 'other demand' load is then added to

the largest one of the following:

1  100% of the nameplate va rating of the cooling load,

2  100% of the nameplate va rating of electric thermal storage and

other heating systems where the usual load is expected to be

continuous at full nameplate value,

3  65% of nameplate va rating of central electric heating,

4  65% of nameplate va rating of less than 4 separately controlled

electric space heating units,

5  40% of nameplate va rating of 4 or more separately controlled

electric space heating units.

The result is the net computed load for this service or feeder.

Data Input

----------

There are 20 data input fields:

Dwelling Square Feet               Attic Fan

Qty. Small App. Ccts               Compactor

Qty Laundry Ccts                   Dishwasher

Heating Load                       Disposal

Cooling Load                       Jacuzzi

Cooktop                            Sump Pump

Range                              Well Pump

Wall Oven                          Other Appliance #1

Dryer                              Other Appliance #2

Water Heater                       Other Lighting Load

Page 4

Use the ENTER, UP, DOWN, TAB or SHIFT+TAB keys to move the cursor

to the desired field, then enter the va value for that load. Note

that the first 3 fields (Dwelling Sq Ft, Qty Small App, & Qty

Laundry) require input other than va values.

Pressing F1 at any time will activate context sensitive help.

Dwelling Square Feet:

Enter the square feet of floor area of the dwelling unit, computed

from the outside dimensions of the building or area. Do not

include open porches, garages or unused or unfinished spaces not

adaptable for future use. NEC 220-3(b).

Quantity Small Appliance Ccts:

Enter the total number of 20 ampere circuits installed to serve

the kitchen, dining room, butler pantry, countertop receptacles.

NEC 220-4.

Quantity Laundry Ccts:

Enter the total number of 20 ampere circuits installed to serve

the laundry area. NEC 220-4.

Heating Load:

Enter 100% of the nameplate va rating of the electric heating

system. After entering a value, press a direction key and a

list menu will apear, prompting you to select the heating system

type.

Cooling Load:

Enter 100% of the nameplate va rating of the electric cooling

system.

Cooktop:

Enter the nameplate va rating of the electric cooktop.

Range:

Enter the nameplate va rating of the electric range.

Wall Oven:

Enter the nameplate va rating of the electric wall oven.

Dryer:

Enter the nameplate va rating of the electric clothes dryer.

Water Heater:

Enter the nameplate va rating of the electric water heater.

Page 5

Attic Fan Thru Well Pump:

Enter the nameplate va rating of the electric appliance.

Other Appliance #1 and #2:

Enter the nameplate va rating of the electric appliance.

After entering a value, press a direction key and a secondary

input area is opened, prompting you for an optional Description,

Motor or Nonmotor load [M/N], Fixed or Nonfixed appliance [F/N].

If this user-defined appliance is a pure motor load (fan motor,

etc.), enter M, else enter N.

If this user-defined appliance is a fixed appliance (pool filter,

etc.), enter Y, else enter N.

When you have completed input in this secondary area, press F2 to

record the data. F1 brings help. Pressing ESC cancels this

appliance, and it will not be included in the calculation.

NOTE: This additional information is not required in the optional

calculation method, since all such loads are combined. However, it

does matter when using the standard method, supported by the

registered-user version of LOADCALC, and I chose to leave it in

this version, for use of the Description field.

Other Lighting Load:

This field can be used to define an additional lighting load which

would not be included in the general lighting category. You can

define it as continuous or noncontinuous.

Enter the va rating of the additional lighting load. After

entering a value, press a direction key and a secondary input area

is opened, prompting you for an optional Description and if it is

a continuous or noncontinuous load [C/N].

If the load is expected to be continuous (3 hours or more), enter

C. The va value you had entered in the previous input area will

be multiplied by 125% in the final calculation.

If the load is expected to be noncontinuous (less than 3 hours),

enter N. The va value you had entered in the previous input area

will be multiplied by 100% in the final calculation.

As you make data entries, a running total is calculated and

displyed towards the bottom of the screen, showing the net

computed load in va and amperes, including all applicable demand

factors. Note that after you input a value in any field, you must

record that value by pressing a direction key, the ENTER key, or a

valid function key.

To view the results of the computation at any time, press F4. The

details of the calculation are printed to the screen, you can PAGE

UP, or DOWN, and pressing ESC will return you to the input area

with all previous data intact.

Page 6

QUICK REFERENCE TABLES:

-----------------------

Grounding Electrode Conductors:

-------------------------------

A quick reference table from NEC Table 250-94, for selecting the

minimum size conductor for grounding AC systems.

To view, from the main menu, select 'Reference' then 'Grounding

Electrode Conductors'. Press ESC to return to the main menu.

Service/Feeder Conductors:

--------------------------

A quick reference table from NEC Section 310, Note 3, for

selecting the minimum size service entrance and feeder conductors

for single phase dwellings.

To view, from the main menu, select 'Reference' then

'Service/Feeder Conductors'. Press ESC to return to the main menu.

SETUP:

------

Color Defaults:

---------------

As shipped, LOADCALC starts up in black and white display (mono)

by default. You can choose to have the program start up in either

mono or color by selecting 'Setup' from the main menu, then select

'Color Display' or 'Mono Display'. Your choice will be executed,

and saved to a disk file, which will automatically be used for

future program use.

Page 7

================================================================

LOADCALC REGISTRATION  Ver. 1.1

----------------------------------------------------------------

When you register your copy of LOADCALC, an expanded 'Registered

User' version of the software will be shipped to you immediately.

That version will support all functions of this shareware

version, plus these additional functions:

* Support of the 'Standard Method' of single dwelling

service/feeder calculations with demand factoring of:

General lighting, small appliance & laundry loads,

Heating & Cooling Loads

Cooktop, range & wall oven

Fixed appliances

Largest motor load

Continuous lighting load

* 2 User definable appliance loads (Motor or nonmotor, fixed or

nonfixed) which will be used in derating and as largest motor

load in the standard method.

* 1 User definable lighting load (continuous or noncontinuous).

* Print routines:

Print output to an ASCII disk file or to a printer. Also will

print up to 4 line header at top of report.

* Unlimited technical support by mail, notice of upgrades, receipt

of future bug fixes.

* Elimination of the program's opening screen.

* See next page for sample printed report.

The registration fee, which includes the expanded registered-user

version of LOADCALC - Ver. 1 is $45.00 per user.

US funds drawn from a US bank only.

Purchase orders without proper fee attached can not be accepted.

To register, return the registration form and fee to:

Robert J. La Capra

50 Hillside Terrace

Andover, NJ 07821

Page 8

Actual printed report from registered-user version of LOADCALC

STANDARD SERVICE/FEEDER LOAD CALCULATION - One Family Dwelling

Bill Handelson

43 High Plains Road

Green Twsp, NJ 89765

Block 55, Lot 19

General Lighting ... : 3200 Sq. Feet x    3 VA =  9600 VA

Small Appliance .... :    2 Circuits x 1500 VA =  3000 VA

Laundry ............ :    1 Circuits x 1500 VA =  1500 VA

---------------------------------------------------------

Total General Light & Small Appliance ........ : 14100 VA

The First   3000 VA @ 100%  =   3000 VA

Remaining  11100 VA @  35%  =   3885 VA

---------------------------------------

GENERAL LIGHTING, SMALL APPLIANCE & LAUNDRY DEMAND LOAD ..... :  6885 VA

Heating Demand ..... : 10000 VA @ 100% = 10000 VA

Cooling Demand ..... :  6000 VA @ 100% =  6000 VA

LARGER OF HEATING OR COOLING DEMAND LOADS (Heating) ......... : 10000 VA

Cooktop ................. :  5000 VA

Range ................... : 12000 VA

Wall Oven ............... :  4000 VA

COOKING EQUIPMENT DEMAND LOAD ............................... : 13850 VA

Dryer ................... :  5000 VA

DRYER DEMAND LOAD ........................................... :  5000 VA

Water Heater ............ :  5500 VA

Attic Fan ............... :  1100 VA

Compactor ............... :   600 VA

Dishwasher .............. :  1200 VA

Disposal ................ :   500 VA

Jacuzzi ................. :  1000 VA

Sump Pump ............... :  1100 VA

Well Pump ............... :  1200 VA

Other Appliance #1 ...... :   500 VA  [ Septic Ejector Pump ]

Other Appliance #2 ...... :   450 VA  [ Gable Exhaust Fan ]

------------------------------------

Fixed Appliance Total ... : 13150 VA

13150 VA @  75% Demand:  9863 VA

FIXED APPLIANCE DEMAND LOAD ................................. :  9863 VA

Largest Motor: Well Pump ............... : @ 1200 VA

25% OF LARGEST MOTOR LOAD ................................... :   300 VA

Other Lighting Load ..... :  1500 VA  [ Barn Lighting ]

NonContinuous Load:  100% Demand

OTHER LIGHTING DEMAND LOAD .................................. :  1500 VA

________________________________________________________________________

NET COMPUTED LOAD ........................................... : 47398 VA

120/240 VOLT SERVICE/FEEDER LOAD ............................ : 197 AMPERES

LOADCALC REGISTRATION FORM

S1236

Registration fee for 1 to 5 users is $45.00 for each user or

machine. Site License & Multiple discounts available for 6 or

more users. Write for info. Purchase orders without payment

attached cannot be accepted. US funds drawn from a US bank.

INCLUDED WITH YOUR REGISTRATION

Disk containing latest program version and documentation file.

Documentation is supplied on disk file. No printed manuals.

One License To Use Software for each user registered.

Unlimited support by US Mail and by CompuServe Mail.

No phone support available.

Shipping via US Postal Service.

Orders shipped same day registration received.

OPTIONAL ITEMS

* UPS Ground Delivery - $10.00 additional per order. Multiple

registrations or registration of LOADCALC and ELECTRC9

together qualify as 1 order, and shipping is $10.00 total.

Supply street address. NO P.O. BOXES.

* 1 Year Of Fax Support for LOADCALC - $10.00 additional per year.

For multiple registrations of LOADCALC, fee is still $10.00

total. Fax # supplied with shipment.

Return This Form And Registration Fee PAYABLE TO:

ROBERT J. LA CAPRA

50 Hillside Terrace

Andover, NJ 07821

S.S.# 137-44-7561

SHIP TO:

Name: _______________________________________________________

Company: ____________________________________________________

Address: ____________________________________________________

City,State,Zip: _____________________________________________

Phone : ______-______-________    Fax : ______-______-_______

Number Of Users: ______ x $45.00 Each = Reg. Fee . : $_______

UPS Ground Shipping - $10.00 Per Order [Optional]  : $_______

1 Year Of LOADCALC Fax Support - $10.00 [Optional] : $_______

_____________________________________________________________

TOTAL FEE ENCLOSED .... : $_______

DISK SIZE PREFERRED:   [   ] 5 1/4"     [   ] 3 1/2"

Page 10

OTHER ELECTRICAL SOFTWARE PROGRAM AVAILABLE

ELECTRC9 Version 9.2

ELECTRC9 is designed to perform most common electrical contracting

and engineering calculations. It is useful to anyone in the

electrical industry - electrical maintenance personnel, lighting

system designers, architects, contractors, engineers, etc. All

functions in ELECTRC9 conform to the 1993 National Electrical Code.

The Registered User Version performs the following functions:

-------------------------------------------------------------

* Power factor correction.

* Voltage drop calculations.

* Short Circuit calculations.

* Device, junction and pull box calcs.

* Conduit size selection for any combination of wire sizes/types.

* Determine the cost to operate loads at different kwh charges.

* Lighting calculations based on the Zonal Cavity Method.

* Motor conductor, overcurrent and overload calculations.

* Wire and conduit size based on allowable voltage drop.

* Quick reference tables for:

Grounding electrode conductor size

Equipment grounding conductor size

Underground cover requirements

KW to ampere tables

Transformer Kva to ampere tables

Metal device box size and capacity

Standard fuse & breaker ratings

Standard pull & junction box table

Wire ampacity table

NEC Temperature limitations

* All functions operate with 'what-if' capability. You can quickly

and easily change only the data you wish to, without having to

start a new calculation and re-enter all the required data.

Results are calculated and displayed as you make each change.

* Three phase support, printed reports, and more are supported in the

expanded 'Registered-User' version shipped upon your registration.

* All functions conform to the 1993 National Electrical Code,

including support of the new NEC Section 110-14(c) - Temperature

Limitation Requirements.

Page 11

ELECTRC9 REGISTRATION FORM

S1236

***  THIS FORM TO BE USED TO REGISTER ELECTRC9 ONLY ***

Registration fee for 1 to 5 users is $59.00 for each user or

machine. Site License & Multiple discounts available for 6 or

more users. Write for info. Purchase orders without payment

attached cannot be accepted. US funds drawn from a US bank.

INCLUDED WITH YOUR REGISTRATION

Latest program version and documentation file.

Documentation is supplied on disk file. No printed manuals.

One License To Use Software for each user registered.

Unlimited support by US Mail and by CompuServe Mail.

No phone support available.

Shipping via US Postal Service.

Orders shipped same day registration received.

OPTIONAL ITEMS

* UPS Ground Delivery - $10.00 additional per order. Multiple

registrations or registration of ELECTRC9 and LOADCALC

together qualify as 1 order, and shipping is $10.00 total.

Supply street address. NO P.O. BOXES.

* 1 Year Of Fax Support for ELECTRC9 - $10.00 additional per year.

For multiple registrations of ELECTRC9, fee is still $10.00

total. Fax # supplied with shipment.

Return This Form And Registration Fee PAYABLE TO:

ROBERT J. LA CAPRA

50 Hillside Terrace

Andover, NJ 07821

S.S.# 137-44-7561

SHIP TO:

Name: _______________________________________________________

Company: ____________________________________________________

Address: ____________________________________________________

City,State,Zip: _____________________________________________

Phone : ______-______-________    Fax : ______-______-_______

Number Of Users: ______ x $59.00 Each = Reg. Fee . : $_______

UPS Ground Shipping - $10.00 Per Order [Optional]  : $_______

1 Year Of ELECTRC9 Fax Support - $10.00 [Optional] : $_______

_____________________________________________________________

TOTAL FEE ENCLOSED .... : $_______

DISK SIZE PREFERRED:   [   ] 5 1/4"     [   ] 3 1/2"